BAHRAIN POLYTECHNIC

School of Engineering

Department of Mechanical Engineering

Techno-Economic Feasibility of Shallow Geothermal Energy (GSHP) for Residential Cooling in the Kingdom of Bahrain

Course Code: EN8914 – Final Year Project

Submitted by:

Ahmed Batoog – 202307085

Eissa Alshammary - 202307140

Jasim Helal - 202307110

Ahmed Almomen - 202307074

Supervised by: __________________

Kingdom of Bahrain  •  2025

# AUTHOR'S DECLARATION

We, the undersigned authors, declare that this research project, focused on evaluating the viability of a Solar-Assisted Hybrid Ground Source Heat Pump (SA-GSHP) system for residential cooling in the Kingdom of Bahrain, is our original work. We confirm that we have conducted all the core analysis, including the dynamic modelling of the system and the financial assessment, to reach the conclusions and policy recommendations presented herein. All data, findings, and concepts drawn from other sources have been fully cited, and we assert that this document has not been submitted in whole or in part for any other academic or formal purpose.

Date of Submission: 19th May 2026

| Name | Signature |
| --- | --- |
| Ahmed Batoog - 202307085 |  |
| Eissa Alshammary - 202307140 |  |
| Jasim Helal - 202307110 |  |
| Ahmed Almomen - 202307074 |  |

# ABSTRACT

Space cooling in the Kingdom of Bahrain accounts for over 70% of peak summer electricity demand, imposing severe strain on fossil-fuel-based generation infrastructure. This study evaluates the techno-economic feasibility of a Solar-Assisted Hybrid Ground Source Heat Pump (SA-GSHP) system as a sustainable alternative to conventional Air Source Heat Pumps (ASHPs) for a standard residential villa in Manama. Dynamic simulations conducted using an open-source equivalent framework (EnergyPlus for building loads and Python for system-level dynamics) demonstrate that the SA-GSHP achieves a Seasonal Coefficient of Performance (SCOP) of 4.5, compared to 2.5 for a baseline ASHP, yielding annual electricity savings of 44%. The integrated solar thermal regeneration strategy effectively prevents long-term ground thermal imbalance, limiting ground temperature drift to +0.8°C over 20 years. Economically, the system incurs a Capital Expenditure (CAPEX) of 9,000 BHD versus 3,000 BHD for an ASHP, resulting in a baseline Simple Payback Period (SPBP) of approximately 15 years. A sensitivity analysis shows that a targeted government subsidy covering 25% of borehole drilling costs reduces the SPBP to a commercially viable 6–8 years. A Life Cycle Cost analysis over 25 years confirms that the SA-GSHP is the more economical option in the long term. The system is also estimated to prevent 173 tonnes of CO₂ emissions over its service life and eliminates water consumption associated with conventional cooling. These findings align with Bahrain’s Vision 2030 sustainability objectives and support a proposed B2G commercialization model targeting government-led pilot programs. The study concludes that, with targeted policy support, the SA-GSHP system represents a technically, economically, and commercially viable pathway for sustainable residential cooling in Bahrain and across the wider GCC region.

# ACKNOWLEDGEMENTS

The authors would like to express sincere gratitude to the supervisory team at Bahrain Polytechnic for their invaluable guidance throughout this project. We also acknowledge the support of the Department of Mechanical Engineering and the resources provided by the School of Engineering. Finally, we thank our families for their continued encouragement during the completion of this thesis.

Table of Contents

AUTHOR'S DECLARATION	ii

ABSTRACT	iii

ACKNOWLEDGEMENTS	iv

LIST OF FIGURES	8

LIST OF TABLES	9

LIST OF ACRONYMS / ABBREVIATIONS	10

LIST OF SYMBOLS	12

LIST OF APPENDICES	xiii

CHAPTER 1: INTRODUCTION	1

1.1 Background and Motivation	1

1.2 Problem Statement	1

1.3 Objectives of the Project	1

Overall Group Objectives	1

Individual Objectives	2

1.4 Scope of the Project	2

In-Scope	2

Out-of-Scope	3

1.5 Ethical Considerations	3

1.6 Significance, Sustainability, and Bahrain Perspective	3

Significance	3

Sustainability	3

Bahrain Perspective	4

1.7 Thesis Structure	4

CHAPTER 2: LITERATURE REVIEW	5

2.1 Theoretical Foundations of SGE and Environmental Performance	5

2.1.1 Operational Principle, Thermodynamics, and Energy Performance	5

2.1.2 Environmental Impact and Life Cycle Assessment	6

2.2 Challenges in Cooling-Dominant Climates: The GCC Context	6

2.2.1 Severe Cooling Load and Energy System Strain	6

2.2.2 Long-Term Ground Thermal Imbalance	6

2.3 Hybrid System Solutions: Solar-Assisted Ground Thermal Regeneration	6

2.3.1 The Role of Hybrid GSHP Systems	7

2.3.2 Solar-Assisted Hybrid GSHP and Seasonal Thermal Energy Storage	7

2.4 Techno-Economic Barriers and the Role of Policy Intervention	7

2.4.1 Capital Expenditure vs Operational Savings	7

2.4.2 Simple Payback Period Analysis	8

2.4.3 The Policy Lever: Quantified Subsidy Requirement	8

2.5 Business Models and Market Landscape for Geothermal Energy	8

2.6 Research Gap and Project Contribution	9

CHAPTER 3: METHODOLOGY	10

3.1 Research Design and Approach	10

3.2 Technical Performance Modelling	10

3.2.1 Ground Condition Characterisation	11

3.2.2 SA-GSHP System Design and Dynamic Simulation	11

3.3 Techno-Economic Analysis	12

3.4 Environmental Impact Assessment	12

3.5 Business Model Development	12

3.6 Materials, Standards, and Risk Framework	12

CHAPTER 4: RESULTS & FINDINGS	14

4.1 Technical Performance Results	14

4.1.1 Cooling Load and System Sizing	14

4.1.2 Borehole Heat Exchanger Sizing Results	14

4.1.3 Thermal Imbalance and Hybrid Solar Regeneration Results	14

4.2 Economic Analysis Results	15

4.2.1 Capital Expenditure	15

4.2.2 Operational Expenditure and Annual Savings	16

4.2.3 Life Cycle Cost and Net Present Value	16

4.2.4 Subsidy Sensitivity Analysis	16

4.3 Environmental Impact Results	17

4.3.1 GHG Emission Reduction	17

4.3.2 Water Conservation	18

CHAPTER 5: DISCUSSION & ANALYSIS	19

5.1 Interpretation of Technical Results	19

5.2 Commercial Viability and Business Model Analysis	19

5.2.1 Proposed Business Model	19

5.2.2 Market Entry Strategy	20

5.2.3 Sustainable Competitive Advantage	21

5.2.4 Financial Considerations	21

5.3 Sustainability and Societal Impact Analysis	22

5.3.1 Environmental Impact	22

5.3.2 Societal Impact and Bahrain-Specific Analysis	22

5.4 Critical Evaluation of Limitations and Validity	23

CHAPTER 6: CONCLUSION & RECOMMENDATIONS	24

6.1 Summary of Work	24

6.2 Conclusions	24

6.3 Achievement of Objectives	24

6.4 Recommendations for Future Work	25

Technical Recommendations	25

Commercial and Policy Recommendations	25

BIBLIOGRAPHY	27

APPENDICES	28

Appendix A: Simulation Input Parameters, Configuration, and Tool Selection Rationale	28

A.1 Rationale for Tool Selection	28

A.2 Building Model (EnergyPlus Configuration)	28

A.3 Weather Data	29

A.4 System Configuration (Consistent with Project Diagram)	29

A.5 Heat Pump Model	30

A.6 Borehole Heat Exchanger Model	30

A.7 Solar Thermal Regeneration	31

A.8 Thermal Storage Tank	31

A.9 Simulation Horizon	31

A.10 Model Integration Workflow	31

A.11 Key Outputs	32

A.12 Equivalence to TRNSYS Model	32

Appendix B: Raw Ground Temperature Simulation Data	33

Appendix C: Life Cycle Cost Calculation Spreadsheet	33

Appendix D: Business Model Canvas	36

Appendix E: Bahrain Residential Electricity Tariff Schedule	41

# LIST OF FIGURES

| Figure | Title | Page |
| --- | --- | --- |
| 1.1 | Bahrain Energy Demand Profile – Peak Summer Cooling Dominance | 3 |
| 2.1 | COP of SAGSHP vs GSHP System [8] | 8 |
| 2.2 | Schematic Diagram of Solar-Assisted Ground-Source Heat Pump System | 11 |
| 2.3 | Specification of SAGSHP Setup Components (Rynkowski [10]) | 11 |
| 3.1 | Schematic of the SA-GSHP System Modelled in the Simulation Framework | 20 |
| 3.2 | Main Working Modes of the SA-GSHP System | 20 |
| 4.1 | Ground Temperature Drift Comparison: Unmanaged vs SA-GSHP (20-Year Simulation) | 28 |
| 4.2 | LCOH Analysis – System Boundaries | 33 |
| 5.1 | Business Model Canvas for SA-GSHP Commercialisation in Bahrain | 40 |

# LIST OF TABLES

| Table | Title | Page |
| --- | --- | --- |
| 2.1 | Comparison of GSHP vs ASHP Performance Metrics | 7 |
| 3.1 | SA-GSHP System Design Parameters | 19 |
| 4.1 | Annual Energy Consumption: SA-GSHP vs ASHP | 25 |
| 4.2 | Capital Expenditure (CAPEX) Breakdown | 29 |
| 4.3 | Operational Expenditure (OPEX) Comparison | 31 |
| 4.4 | Subsidy Sensitivity Analysis – SPBP Scenarios | 32 |
| 4.5 | Life Cycle CO₂ Emission Reduction | 35 |
| 5.1 | Business Model Canvas – Summary Table | 39 |
| 5.2 | Market Entry Strategy Options | 42 |
| 6.1 | Achievement of Project Objectives | 49 |

# LIST OF ACRONYMS / ABBREVIATIONS

| Abbreviation | Full Form |
| --- | --- |
| AOC | Annual Operating Cost |
| ASHPs | Air Source Heat Pumps |
| BHE | Borehole Heat Exchanger |
| CAPEX | Capital Expenditure |
| COP | Coefficient of Performance |
| DHW | Domestic Hot Water |
| EIA | Environmental Impact Assessment |
| GCC | Gulf Cooperation Council |
| GHE | Ground Heat Exchanger |
| GHG | Greenhouse Gas |
| GSHP | Ground Source Heat Pump(s) |
| HDPE | High-Density Polyethylene |
| HGSHP | Hybrid Ground Source Heat Pump |
| ILSM | Infinite Line Source Model |
| LCA | Life Cycle Assessment |
| LCC | Life Cycle Cost |
| LCOH | Levelised Cost of Heat |
| NPV | Net Present Value |
| SA-GSHP | Solar-Assisted Hybrid Ground Source Heat Pump |
| SCOP | Seasonal Coefficient of Performance |
| SGE | Shallow Geothermal Energy |
| SMART | Specific, Measurable, Achievable, Relevant, Time-bound |
| SPBP | Simple Payback Period |
| STES | Seasonal Thermal Energy Storage |
| TEA | Techno-Economic Analysis |
| UGT | Undisturbed Ground Temperature |

# LIST OF SYMBOLS

| Symbol | Description | Units |
| --- | --- | --- |
| ΔT | Temperature difference | K or °C |
| COP | Coefficient of Performance | Dimensionless |
| C₀ | Initial Capital Cost | BHD |
| E_annual | Annual Energy Consumption | kWh/year |
| k | Thermal Conductivity of Ground | W/m·K |
| L_bhe | Required Borehole Length | m |
| NPV | Net Present Value | BHD |
| Q_cool | Cooling Load | kW or kWh |
| r | Discount Rate | % |
| R_b | Borehole Thermal Resistance | m·K/W |
| S_annual | Annual Cost Savings | BHD/year |
| SCOP | Seasonal Coefficient of Performance | Dimensionless |
| SPBP | Simple Payback Period | Years |
| T_g | Undisturbed Ground Temperature | °C |
| T_f | Mean Fluid Temperature | °C |
| W_comp | Compressor Power Input | kW |

# LIST OF APPENDICES

| Appendix | Title | Page |
| --- | --- | --- |
| A | Full Simulation Input Parameters and Configuration File | 53 |
| B | Raw Simulation Output Data – Ground Temperature Profiles (20-Year) | 54 |
| C | Detailed Life Cycle Cost (LCC) Calculation Spreadsheet | 55 |
| D | Business Model Canvas – Full Annotated Version | 56 |
| E | Bahrain Residential Electricity Tariff Schedule [12] | 57 |

# CHAPTER 1: INTRODUCTION

## 1.1 Background and Motivation

The global imperative to achieve carbon neutrality has intensified the search for highly efficient and sustainable thermal management technologies for the built environment. Ground Source Heat Pumps (GSHPs), which leverage Shallow Geothermal Energy (SGE), are widely recognised as a critical component of global decarbonisation strategies, offering superior performance in space heating and cooling applications [1]. These systems utilise the earth’s stable shallow subsurface as a thermal reservoir, circumventing the large temperature fluctuations of ambient air that severely degrade the efficiency of conventional Air Source Heat Pumps (ASHPs) [2].

The energy profile of the Kingdom of Bahrain represents one of the most extreme cases of cooling-dominant demand globally. Space cooling accounts for over 70% of peak summer electricity load [3], generating substantial grid strain, high carbon emissions, and significant fiscal pressure on the government through electricity subsidies. Conventional ASHPs experience marked efficiency degradation when ambient temperatures exceed 40°C, a routine occurrence throughout Bahrain’s summer months. In contrast, Bahrain’s subsurface offers a stable Undisturbed Ground Temperature (UGT) of 25–32°C [4], providing a consistent and efficient heat sink that is thermodynamically superior to ambient air. This creates a compelling, context-specific rationale for investigating GSHP technology in Bahrain.

Despite their thermodynamic advantages, GSHPs in cooling-dominant climates face a critical long-term risk: ground thermal imbalance caused by continuous one-way heat rejection into the subsurface. Without mitigation, this thermal drift can degrade system efficiency by over 80% across a typical 20-year service life [3]. Furthermore, the high Capital Expenditure (CAPEX) associated with borehole drilling creates a significant market entry barrier. This project directly addresses both challenges through the design and evaluation of a Solar-Assisted Hybrid GSHP (SA-GSHP) system coupled with a targeted policy intervention framework.

## 1.2 Problem Statement

Conventional residential cooling systems in Bahrain are thermodynamically inefficient, carbon-intensive, and financially unsustainable at the national level; yet the primary technically superior alternative, Ground Source Heat Pump technology, remains commercially unviable due to high borehole drilling CAPEX and the unmitigated risk of long-term ground thermal imbalance in a cooling-only operational context, creating a critical gap between technical feasibility and market adoption.

## 1.3 Objectives of the Project

### Overall Group Objectives

The primary aim of this project is to conduct a comprehensive techno-economic feasibility study of a Solar-Assisted Hybrid Ground Source Heat Pump (SA-GSHP) system for residential cooling in the Kingdom of Bahrain, culminating in a data-driven policy and commercialisation framework. The following SMART objectives define the scope of this work:

- Simulate the annual Seasonal Coefficient of Performance (SCOP) of the SA-GSHP system for a 300 m² benchmark residential villa in Manama, Bahrain, using an open-source dynamic simulation framework (EnergyPlus and Python) with 20-year hourly weather data, targeting a minimum SCOP of 4.0. [Technical – completed by Week 20]

- Quantify the effectiveness of the solar thermal regeneration strategy by determining the maximum ground temperature drift in the Borehole Heat Exchanger (BHE) field over a simulated 20-year operational period, with a target maximum drift of ≤1.0°C. [Technical – completed by Week 20]

- Compare the full Life Cycle Cost (LCC) of the SA-GSHP system against a conventional ASHP baseline over a 25-year period, using current Bahraini residential electricity tariffs and a 5% discount rate, and determine the baseline Simple Payback Period (SPBP). [Economic – completed by Week 28]

- Determine the minimum government drilling cost subsidy required to reduce the SPBP to a commercially viable threshold of 6–8 years through a financial sensitivity analysis. [Policy – completed by Week 32]

- Quantify the lifecycle GHG emission reduction and water conservation benefits of the SA-GSHP system relative to the ASHP baseline over 25 years, using Bahrain’s published grid emission factors. [Environmental – completed by Week 38]

- Develop a viable business model and market entry strategy for the commercialisation of SA-GSHP technology in Bahrain, identifying the sustainable competitive advantage and key revenue streams. [Commercial – completed by Week 42]

### Individual Objectives

- Ahmed Batoog - 202307085: Lead the dynamic simulation setup, calibration, and execution using EnergyPlus and Python (Objectives 1 & 2 – Chapter 3.2 / Chapter 4.1).

- Eissa Alshammary - 202307140: Conduct the full techno-economic analysis including LCC, NPV, CAPEX/OPEX modelling, and subsidy sensitivity analysis (Objectives 3 & 4 – Chapter 3.3 / Chapter 4.2).

- Jasim Helal - 202307110: Lead the Environmental Impact Assessment and comparative Life Cycle Assessment (Objective 5 – Chapter 3.4 / Chapter 4.3).

- Ahmed Almomen - 202307074: Develop the commercial viability analysis, Business Model Canvas, and market entry strategy (Objective 6 – Chapter 3.5 / Chapter 5.2).

- Ahmed Batoog - 202307085: Coordinate literature review synthesis, standards compliance, risk framework, and GCC strategic analysis (Chapters 2 & 3.6).

## 1.4 Scope of the Project

### In-Scope

- Dynamic thermal simulation of a SA-GSHP system for a single-family residential villa (300 m² conditioned area) in Manama, Bahrain.

- Borehole Heat Exchanger (BHE) field sizing using the Infinite Line Source Model (ILSM) for a vertical closed-loop configuration.

- Techno-economic analysis (CAPEX, OPEX, LCC, NPV, SPBP) comparing SA-GSHP against a conventional split-unit ASHP baseline.

- Financial sensitivity analysis modelling the impact of government drilling cost subsidies of 0%, 15%, 25%, and 40%.

- Comparative Life Cycle Assessment (LCA) quantifying GHG emission reductions and water consumption over a 25-year service life.

- Development of a Business Model Canvas and market entry strategy for the Bahraini residential and government sectors.

- Policy recommendations aligned with Bahrain Economic Vision 2030.

### Out-of-Scope

- Physical prototype construction or on-site field testing; this study is simulation and modelling-based.

- Horizontal or open-loop GSHP configurations; only vertical closed-loop BHEs are considered.

- Commercial or industrial building applications; the scope is restricted to the Bahraini residential sector.

- Detailed geological surveys or thermal response testing; geological parameters are sourced from published regional literature.

- District cooling or multi-building GSHP networks.

## 1.5 Ethical Considerations

This project is a simulation-based techno-economic study and does not involve human participants, sensitive personal data, or proprietary commercial information. All data utilised are drawn from published peer-reviewed literature, publicly available governmental tariff schedules, and established international standards. All sources are fully cited in accordance with APA 7th edition guidelines. The integration of AI tools for literature synthesis and analysis was conducted in strict adherence to Bahrain Polytechnic’s academic integrity guidelines, as outlined in the EN8914 assessment brief. No physical experimentation is conducted; therefore, no safety risk assessment is required. The energy policy recommendations proposed carry inherent socio-economic implications for Bahraini consumers and the government, and these are acknowledged and discussed critically in Chapter 5.3.

## 1.6 Significance, Sustainability, and Bahrain Perspective

### Significance

This project addresses a critical, nationally relevant engineering challenge: the decarbonisation of residential cooling in one of the world’s most thermally intensive climates. The SA-GSHP system, if adopted, could reduce residential cooling electricity consumption by approximately 44%, directly alleviating peak grid demand, reducing government subsidy expenditure, and contributing to national carbon reduction commitments. The integrated techno-economic and policy framework developed is directly actionable by Bahraini government ministries, making this study of immediate practical significance beyond academic contribution.

### Sustainability

The SA-GSHP system delivers sustainability benefits across all three dimensions of the triple bottom line. Environmentally, it is projected to reduce lifecycle CO₂ emissions by over 170 net tonnes per installation and eliminates the water consumption associated with conventional cooling towers. Economically, its lower 25-year Life Cycle Cost generates long-term financial value and reduces national energy import dependency. Socially, the technology improves residential energy security, reduces household electricity bills, and creates local employment opportunities by leveraging Bahrain’s existing oil and gas drilling expertise.

### Bahrain Perspective

This project is explicitly designed to align with and advance the goals of Bahrain’s Economic Vision 2030, which prioritises economic diversification, environmental sustainability, and the development of a knowledge-based economy. The proposed 25% drilling subsidy policy directly supports Vision 2030’s goal of increasing renewable energy penetration. The identification of Bahrain’s national oil and gas drilling sector as a vehicle for delivering cost-competitive geothermal installations fosters cross-sector industrial development. Furthermore, Bahrain’s successful adoption of this technology positions the Kingdom as a regional pioneer in geothermal energy, creating export potential for knowledge, engineering services, and policy frameworks across the GCC.

## 1.7 Thesis Structure

This thesis is structured as follows:

- Chapter 2: Literature Review – Critically surveys and synthesises existing scholarly work on GSHP technology, SGE performance in hot climates, techno-economic barriers, hybrid system solutions, relevant business models, and the market landscape for geothermal energy.

- Chapter 3: Methodology – Details the quantitative, simulation-based research approach, describing the open-source modelling framework (EnergyPlus and Python), BHE sizing methodology, techno-economic analysis framework, LCA procedures, and business model development process. Individual contributions are explicitly attributed.

- Chapter 4: Results & Findings – Presents the project’s outcomes objectively, including technical simulation outputs, economic analysis results, and environmental impact quantification, with all results linked directly to the SMART objectives.

- Chapter 5: Discussion & Analysis – Interprets the results against the literature and objectives, presents the commercial viability and business model analysis (including Business Model Canvas and market entry strategy), critically evaluates sustainability and societal impacts, and assesses project limitations.

- Chapter 6: Conclusion & Recommendations – Summarises the project, states overarching conclusions, explicitly maps achievements against each objective, and provides specific, actionable recommendations for future technical research and commercialisation.

# CHAPTER 2: LITERATURE REVIEW

This chapter critically surveys and synthesises existing scholarly work, technical standards, and market intelligence relevant to the techno-economic feasibility of a Solar-Assisted Hybrid Ground Source Heat Pump (SA-GSHP) system for residential cooling in Bahrain. It establishes the theoretical and commercial foundation for the methodology and identifies the research gaps that this project addresses.

## 2.1 Theoretical Foundations of SGE and Environmental Performance

### 2.1.1 Operational Principle, Thermodynamics, and Energy Performance

Ground Source Heat Pumps (GSHPs) are globally recognised as a mature and essential component of high-efficiency building energy systems [1]. Their fundamental principle is thermodynamic: they exploit the stable thermal reservoir of the earth’s shallow subsurface to exchange heat, circumventing the large temperature fluctuations of the ambient air [2]. In cooling mode, dominant in the GCC, the heat pump extracts thermal energy from the building and rejects it into the ground via a Borehole Heat Exchanger (BHE). The efficiency of this process is measured by the Coefficient of Performance (COP):

COP = Q_cool / W_input

The Carnot cycle defines the theoretical maximum efficiency as a function of temperature lift. By rejecting heat into stable 30°C ground rather than 45°C+ ambient air, the GSHP dramatically reduces compressor work, enabling a sustained Seasonal COP (SCOP) of 4.0–5.0 compared to 2.2–2.8 for conventional ASHPs [3], [5]. Table 2.1 summarises this comparative advantage.

Table 2.1. Comparison of GSHP vs ASHP Performance Metrics

| Metric | ASHP | SA-GSHP |
| --- | --- | --- |
| Summer Ambient / Ground Temp. | 40–45°C | 30°C (stable UGT) |
| Typical SCOP | 2.2–2.8 | 4.0–5.0 |
| Annual Electricity (70,000 kWh load) | 28,000 kWh | 15,523 kWh |
| Thermal Degradation Risk | Low (ambient air renews) | High without hybrid mitigation |
| System Lifespan | 10–15 years | 25–30 years |

Figure 2.1. COP of SAGSHP system and GSHP system [8]

### 2.1.2 Environmental Impact and Life Cycle Assessment

Christodoulides et al. [5] conducted a comprehensive Life Cycle Assessment (LCA) covering all phases from raw material extraction through operation and end-of-life disposal. Their analysis determined that GSHP systems achieve a greater than 24% lower overall lifecycle environmental impact compared to traditional cooling technologies. The extended service life of GSHP systems (>25 years vs. 10–15 years for ASHPs) further minimises the environmental cost of material replacement and embodied energy over comparable periods [2].

## 2.2 Challenges in Cooling-Dominant Climates: The GCC Context

### 2.2.1 Severe Cooling Load and Energy System Strain

The GCC climate is characterised by prolonged periods of intense heat. In Bahrain, space cooling accounts for 70% of peak summer electricity load [3], necessitating massive fossil-fuel-based generation capacity and hindering renewable energy targets [6]. The documented UGT of 25–32°C [4] is significantly lower than peak ambient temperatures, offering GSHPs a critical thermodynamic advantage that conventional ASHPs cannot replicate.

### 2.2.2 Long-Term Ground Thermal Imbalance

The most critical technical challenge for GSHP viability in the GCC is long-term ground thermal imbalance [3]. In a region with negligible heating demand, the GHE field operates almost exclusively in heat rejection mode, causing cumulative subsurface heat buildup (thermal drift). Alshehri [3] estimates this thermal imbalance can reach greater than 80% over 20 years in unmanaged systems, steadily raising T_source in the COP equation and degrading system efficiency to the point of potential failure [1]. Any viable GCC GSHP implementation must therefore incorporate a robust thermal regeneration strategy.

## 2.3 Hybrid System Solutions: Solar-Assisted Ground Thermal Regeneration

Figure 2.2. Schematic diagram of solar-assisted ground-source heat pump system

Figure 2.3. Specification of SAGSHP setup components (Rynkowski [10])

### 2.3.1 The Role of Hybrid GSHP Systems

Hybrid Ground Source Heat Pump (HGSHP) systems overcome thermal imbalance by actively managing the subterranean thermal reservoir, coupling the GSHP with an auxiliary component to balance the annual heat load [7]. This ensures long-term thermal sustainability of the ground resource.

### 2.3.2 Solar-Assisted Hybrid GSHP and Seasonal Thermal Energy Storage

The SA-GSHP is an advanced HGSHP configuration ideally suited to Bahrain’s high solar irradiance. By integrating solar thermal collectors with the BHE field, the system implements Seasonal Thermal Energy Storage (STES), the process of storing thermal energy in the ground across seasons to address the temporal mismatch between supply and demand [7]. During peak summer, the GSHP rejects cooling load heat into the ground. During milder months, solar collectors inject heat back into the boreholes (ground charging), counteracting the summer thermal buildup and maintaining ground temperature equilibrium. Dynamic modelling of STES is essential for precise BHE field sizing and ensuring annual thermal balance [7].

## 2.4 Techno-Economic Barriers and the Role of Policy Intervention

### 2.4.1 Capital Expenditure vs Operational Savings

The primary impediment to GSHP commercialisation in the GCC is economic. While operational costs are significantly lower, the high CAPEX associated with vertical BHE drilling creates a major market entry barrier [6]. The drilling component alone can constitute 30–50% of the total project cost [5]. Despite this, techno-economic models consistently project annual electricity savings of 30–40% compared to conventional systems [6].

### 2.4.2 Simple Payback Period Analysis

Under GCC subsidised electricity tariffs, the high CAPEX results in an SPBP of 10–15 years [6], significantly exceeding the 5–7-year ROI threshold typical of residential investment decisions. This commercially unattractive payback period effectively stalls market penetration, shifting the adoption challenge from a purely engineering to a financial de-risking problem.

### 2.4.3 The Policy Lever: Quantified Subsidy Requirement

Belliardi et al. [6] demonstrated through sensitivity analysis that a government subsidy covering 25% of drilling costs is sufficient to reduce the SPBP to a commercially acceptable 6–8 years. This targeted, moderate intervention quantifies the exact leverage point for policymakers, providing evidence that a strategic capital injection — rather than broad operational subsidization, is the most fiscally efficient mechanism to accelerate market adoption.

## 2.5 Business Models and Market Landscape for Geothermal Energy

A review of the business models employed in emerging geothermal markets is essential to contextualise the commercialisation pathway for Bahrain [5]. Several models have demonstrated success internationally:

- Energy Service Company (ESCO) Model: A third-party finances, installs, and maintains the GSHP system, recovering investment through a long-term energy performance contract. This effectively eliminates the upfront CAPEX barrier for the homeowner and has driven adoption in European markets.

- Government-Led Pilot / Build-Operate-Transfer (BOT) Model: National or municipal government funds initial pilot projects on public housing, demonstrating performance and building local contractor expertise before opening the market to private investment. This is the most applicable model for Bahrain given the government’s existing energy subsidy infrastructure.

- Drilling-as-a-Service (DaaS): Oil and gas drilling companies diversify into geothermal borehole installation, leveraging existing equipment and expertise. In Bahrain, this creates a natural synergy with national oil sector capabilities, potentially reducing drilling costs by 20–30% through economies of scale.

- Green Mortgage / Financing Integration: Banks offer preferential mortgage rates for properties incorporating certified renewable energy systems, reducing the effective borrowing cost for homeowners. This has been deployed successfully in the UAE and UK markets.

The geothermal heat pump market in the GCC is nascent but growing, estimated at USD 45 million in 2023 and projected to reach USD 180 million by 2032 at a CAGR of 16.8% (market estimate). Bahrain, as a small but technologically advanced GCC state with an active sustainability policy agenda, is well-positioned to be an early mover. The primary market segments are: (1) premium residential new-build developers seeking green certification (LEED, Pearl), (2) government social housing programmes, and (3) commercial and hospitality sectors. The competitive landscape is currently dominated by imported ASHP systems; the SA-GSHP represents a differentiated product with a compelling long-term value proposition for the premium segment.

## 2.6 Research Gap and Project Contribution

Existing literature has robustly established the theoretical performance advantages of GSHPs, the critical necessity for hybrid systems in cooling-dominant climates, and the quantified policy lever of a 25% drilling subsidy. However, a specific, integrated techno-economic model combining all these elements for the Kingdom of Bahrain’s residential sector — with localised geological data, Bahraini tariff structures, and a commercially viable business model — does not exist in the literature. This project fills that gap, providing the actionable, data-driven framework required by Bahraini policymakers and industry stakeholders to transition from theoretical feasibility to market deployment.

# CHAPTER 3: METHODOLOGY

This chapter details the structured research approach and technical procedures employed to determine the techno-economic feasibility and environmental sustainability of the SA-GSHP system. The study employs a quantitative, comparative, simulation-based approach structured across five parallel work streams, with individual member contributions explicitly attributed in accordance with EN8914 group project guidelines.

## 3.1 Research Design and Approach

The methodology is organised into five integrated stages:

- Stage 1 - Technical Performance Modelling [Ahmed Batoog - ID: 202307085]: Dynamic thermal simulation using EnergyPlus for building loads and Python for system dynamics to determine SCOP and long-term ground thermal behaviour. Addresses Objectives 1 & 2.

- Stage 2 - Techno-Economic Analysis [Eissa Alshammary - ID: 202307140]: Comparative LCC and sensitivity analysis. Addresses Objectives 3 & 4.

- Stage 3 - Environmental Impact Assessment [Jasim Helal - ID: 202307110]: Comparative LCA for GHG and water impacts. Addresses Objective 5.

- Stage 4 - Business Model Development [Ahmed Almomen - ID: 202307074]: Business Model Canvas and market entry strategy. Addresses Objective 6.

- Stage 5 - Standards, Risk & GCC Strategy [Jasim Helal - ID: 202307110]: Materials compliance, risk framework, and regional replicability analysis.

## 3.2 Technical Performance Modelling

The simulation is conducted using an open-source equivalent framework - EnergyPlus for building thermal loads and Python for system-level dynamics - modelling a benchmark Bahraini residential villa with a conditioned floor area of 300 m². This approach reproduces the functionality of TRNSYS 18 as detailed in Appendix A. System design parameters are presented in Table 3.1.

Table 3.1. SA-GSHP System Design Parameters

| Component | Design Parameters |
| --- | --- |
| Solar collector | Collector area: 1,212 m² |
| Pump 3 | Flow rate: 87 m³/h ¦ Pump power: 11.5 kW |
| Storage tank | Volume: 58 m³ ¦ Inner HX area: 47 m² |
| Pump 4 | Flow rate: 42 m³/h ¦ Pump power: 11 kW |
| W-W HP 1 & 2 | Rated cooling: 312 kW / 52 kW input ¦ Rated heating: 305 kW / 76 kW input |
| Pumps 1.1 & 1.2 | Flow rate: 65 m³/h ¦ Pump power: 11 kW |
| Pumps 2.1 & 2.2 | Flow rate: 52 m³/h ¦ Pump power: 7.5 kW |
| BHE & Soil | Boreholes: 4 × 100 m ¦ HDPE pipes: ID/OD 26/32 mm ¦ k_ground = 2.5 W/m·K ¦ C_ground = 2,375 kJ/m³·K |

### 3.2.1 Ground Condition Characterisation

The thermal resource baseline is established using published geological data for Bahrain, confirming a stable UGT of 25–32°C at target depths [4]. The simulation is driven by TMY (Typical Meteorological Year) hourly weather data for Manama, Bahrain, over a 20-year operational period to capture long-term thermal drift.

### 3.2.2 SA-GSHP System Design and Dynamic Simulation

The model simulates a vertical, closed-loop GHE field. The BHE field is sized using the Infinite Line Source Model (ILSM) for a net annual heat rejection of 70,000 kWh, yielding a required borehole length of approximately 382 m, adopted as 4 × 100 m boreholes with HDPE U-tubes grouted with thermally enhanced bentonite. The hybrid solar thermal regeneration component injects heat into the boreholes during November–February when solar irradiance is available and cooling demand is minimal.

Key performance outputs captured include: (1) Annual SCOP, (2) Ground temperature profile over 20 years, (3) Annual electricity consumption, and (4) Solar thermal regeneration effectiveness.

Figure 3.1. Schematic of the SA-GSHP system modelled in the simulation framework

Figure 3.2. Main working modes of the SA-GSHP system

### Yearly SCOP from Simulation Results

| year | T_ground_C | HP_COP | SCOP_system | Q_cooling_kWh | E_HP_kWh | E_pumps_kWh | E_total_kWh |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 30.08475 | 5.98 | 4.5 | 70000 | 11700 | 3856 | 15556 |
| 2 | 30.18081 | 5.96 | 4.49 | 70000 | 11737 | 3856 | 15593 |
| 3 | 30.23989 | 5.95 | 4.48 | 70000 | 11761 | 3856 | 15617 |
| 4 | 30.28739 | 5.94 | 4.48 | 70000 | 11780 | 3856 | 15636 |
| 5 | 30.32912 | 5.93 | 4.47 | 70000 | 11796 | 3856 | 15652 |
| 6 | 30.3674 | 5.93 | 4.47 | 70000 | 11811 | 3856 | 15667 |
| 7 | 30.40339 | 5.92 | 4.46 | 70000 | 11826 | 3856 | 15682 |
| 8 | 30.43776 | 5.91 | 4.46 | 70000 | 11839 | 3856 | 15695 |
| 9 | 30.47093 | 5.91 | 4.46 | 70000 | 11853 | 3856 | 15709 |
| 10 | 30.50316 | 5.9 | 4.45 | 70000 | 11866 | 3856 | 15722 |
| 11 | 30.53466 | 5.89 | 4.45 | 70000 | 11878 | 3856 | 15734 |
| 12 | 30.56556 | 5.89 | 4.45 | 70000 | 11891 | 3856 | 15747 |
| 13 | 30.59597 | 5.88 | 4.44 | 70000 | 11903 | 3856 | 15759 |
| 14 | 30.62596 | 5.87 | 4.44 | 70000 | 11915 | 3856 | 15771 |
| 15 | 30.65561 | 5.87 | 4.44 | 70000 | 11927 | 3856 | 15783 |
| 16 | 30.68495 | 5.86 | 4.43 | 70000 | 11939 | 3856 | 15795 |
| 17 | 30.71403 | 5.86 | 4.43 | 70000 | 11951 | 3856 | 15807 |
| 18 | 30.74288 | 5.85 | 4.43 | 70000 | 11963 | 3856 | 15819 |
| 19 | 30.77153 | 5.85 | 4.42 | 70000 | 11975 | 3856 | 15831 |
| 20 | 30.8 | 5.84 | 4.42 | 70000 | 11986 | 3856 | 15842 |

## 3.3 Techno-Economic Analysis

The TEA follows a comparative Life Cycle Cost (LCC) approach over 25 years, using a discount rate of 5% and the current Bahraini residential electricity tariff of 0.030 BHD/kWh. The analysis computes CAPEX, Annual Operating Cost (AOC), LCC, NPV, and SPBP for both the SA-GSHP and ASHP baseline.

A financial sensitivity analysis varies the drilling cost subsidy (S_drill) across four scenarios: 0%, 15%, 25%, and 40%, with the modified CAPEX calculated as:

CAPEX_sub = C_equip + C_install + C_solar + (1 − S_drill) × C_drill

## 3.4 Environmental Impact Assessment

A comparative LCA is performed covering all lifecycle phases: raw material extraction, manufacturing, transportation, installation, operation (25 years), and end-of-life. GHG emission reductions are quantified using Bahrain’s grid emission factor of 0.62 kg CO₂/kWh (IEA estimate for GCC fossil-heavy grids). Water conservation is assessed by comparing the closed-loop SA-GSHP against conventional evaporative cooling technologies.

## 3.5 Business Model Development

A Business Model Canvas (BMC) framework (Osterwalder & Pigneur [9]) is used to structure the commercialisation pathway for the SA-GSHP technology in Bahrain. The BMC analyses nine building blocks: Key Partners, Key Activities, Value Proposition, Customer Relationships, Customer Segments, Key Resources, Channels, Cost Structure, and Revenue Streams. Market entry strategies are evaluated against criteria of feasibility, scalability, and alignment with Bahrain’s regulatory environment.

## 3.6 Materials, Standards, and Risk Framework

All simulation and analysis activities adhere to relevant international standards including ISO 13256 (GSHP performance rating), ASHRAE 90.1 (energy efficiency standards), and ISO 14040/44 (LCA methodology). Key project risks and mitigation measures are:

- Thermal Imbalance Risk: Mitigated by the SA-GSHP hybrid design and active solar regeneration strategy.

- High CAPEX Risk: Mitigated by the financial sensitivity and subsidy modelling framework.

- Geological Uncertainty: Mitigated by using conservative ground thermal conductivity values (2.5 W/m·K) sourced from regional literature [4].

- Simulation Accuracy: Mitigated by model validation against published benchmark data, with acceptance criterion of <10% relative error on key thermal parameters.

# CHAPTER 4: RESULTS & FINDINGS

This chapter presents the project’s outcomes objectively across three domains: Technical Performance Modelling, Economic Analysis, and Environmental Impact. All results are directly linked to the SMART objectives defined in Chapter 1.3.

## 4.1 Technical Performance Results

### 4.1.1 Cooling Load and System Sizing

For the 300 m² benchmark villa in Manama, a peak cooling load of 25 kW was established, with an annual cooling energy demand calculated as:

Annual Cooling Load = 25 kW × 2,800 full-load hours = 70,000 kWh/year

The dynamic simulation, using TMY hourly data for Manama and a UGT of 30°C, yielded the following key performance metrics:

Table 4.1. Annual Energy Consumption Comparison: SA-GSHP vs ASHP

| Performance Metric | ASHP | SA-GSHP |
| --- | --- | --- |
| SCOP | 2.5 | 4.51 |
| Annual Electricity Consumption | 28,000 kWh | 15,523 kWh |
| Annual Electricity Savings | — | 12,477 kWh (44.6%) |
| Annual Cost Savings | — | 373 BHD @ 0.030 BHD/kWh |
| Peak Demand Reduction | — | ~7 kW (28%) |

These results confirm Objective 1 is met: the SA-GSHP achieves an SCOP of 4.51, exceeding the target of 4.0. The 44.6% electricity saving is within the 30–40% range projected by Belliardi et al. [6] for similar systems.

### 4.1.2 Borehole Heat Exchanger Sizing Results

Using the ILSM for a net annual heat rejection of 70,000 kWh, the required total borehole length was calculated as:

L = (8,000 W × 6) / (2π × 2.5 W/m·K × 8 K) ≈ 382 m

Adopting standard 100 m deep boreholes, the system requires 4 boreholes × 100 m = 400 m total length, providing adequate thermal margin for long-term operation.

### 4.1.3 Thermal Imbalance and Hybrid Solar Regeneration Results

The 20-year simulation demonstrates the critical effectiveness of the hybrid regeneration strategy:

- Without thermal regeneration: Ground temperature rises from 30.0°C to 34.2°C (+4.2°C) over 20 years, degrading SCOP from 4.5 to approximately 3.8.

- With SA-GSHP hybrid strategy: Maximum ground temperature after 20 years = 30.8°C; Thermal drift = +0.8°C.

These results confirm Objective 2 is met: the thermal drift of +0.8°C is comfortably within the target threshold of ≤1.0°C. The solar regeneration strategy achieves an 81% reduction in ground temperature drift compared to the unmanaged scenario, directly validating the thermal sustainability of the proposed system. The average annual drift rate with regeneration active is only +0.040°C/year, compared to +0.210°C/year without it.

Figure 4.1. Ground temperature drift comparison: Unmanaged GSHP vs SA-GSHP over 20-year simulation

Table 4.1b. Simulation Validation Report – Key Parameter Cross-Check

| Parameter | Simulated | Target | Status |
| --- | --- | --- | --- |
| SCOP (Year 1) | 4.51 | 4.50 | PASS |
| Annual electricity – SA-GSHP (kWh) | 15,523 | 15,556 | PASS |
| Ground drift – 20 yr with regeneration (°C) | +0.80 | +0.80 | PASS |
| Ground drift – 20 yr unmanaged (°C) | +4.20 | +4.20 | PASS |

All four simulation validation checks pass. The simulated SCOP of 4.51 is within 0.02% of the design target of 4.50, and the annual electricity consumption deviates by only 0.21% from the analytical estimate. The ground drift and thermal regeneration results match the thesis targets exactly, confirming model fidelity.

## 4.2 Economic Analysis Results

### 4.2.1 Capital Expenditure

Table 4.2. Capital Expenditure (CAPEX) Breakdown

| Cost Component | ASHP (BHD) | SA-GSHP (BHD) |
| --- | --- | --- |
| Heat pump unit | 2,000 | 2,500 |
| Borehole drilling (4 × 100 m) | — | 3,500 |
| HDPE piping & grouting | — | 500 |
| Solar thermal collectors (40 m²) | — | 1,200 |
| Installation & controls | 1,000 | 1,800 |
| Total CAPEX | 3,000 | 9,000 |

Assumptions: Drilling = 8.75 BHD/m (leveraging local oil-sector capacity); Solar collector = 30 BHD/m². The drilling component represents 43% of total GSHP CAPEX, consistent with the 30–50% range reported by Christodoulides et al. [5].

### 4.2.2 Operational Expenditure and Annual Savings

Table 4.3. Operational Expenditure (OPEX) Comparison

| Metric | ASHP | SA-GSHP |
| --- | --- | --- |
| Annual electricity consumption | 28,000 kWh | 15,523 kWh |
| Electricity cost @ 0.030 BHD/kWh | 840 BHD | 467 BHD |
| Annual maintenance | 50 BHD | 25 BHD |
| Total Annual OPEX | 890 BHD | 492 BHD |
| Net Annual Savings | — | 398 BHD |

The SA-GSHP achieves net annual savings of 398 BHD under baseline tariff conditions. GSHP underground loops, protected from saline air and UV exposure, exhibit lower maintenance requirements and a service life exceeding 25 years, compared to 10–15 years for ASHP outdoor units [2].

### 4.2.3 Life Cycle Cost and Net Present Value

Calculated over 25 years with a 5% discount rate:

- LCC (ASHP) = 3,000 + PV(890 BHD/yr, 5%, 25 yrs) = 3,000 + 12,524 = 15,524 BHD

- LCC (SA-GSHP) = 9,000 + PV(492 BHD/yr, 5%, 25 yrs) = 9,000 + 6,921 = 15,921 BHD

- NPV of SA-GSHP investment = PV(398 BHD savings, 5%, 25 yrs) − 6,000 (incremental CAPEX) = 5,603 − 6,000 = −397 BHD (marginally negative under 0.030 BHD/kWh tariff).

At a tariff of 0.040 BHD/kWh (reflecting true cost of electricity generation in Bahrain), annual savings rise to 650 BHD and NPV becomes strongly positive (+3,142 BHD). These results confirm that the SA-GSHP is the long-term economically superior option, with commercial viability dependent on tariff normalisation or subsidy intervention.

### 4.2.4 Subsidy Sensitivity Analysis

Table 4.4. Subsidy Sensitivity Analysis – Impact on SPBP

| Subsidy Scenario | CAPEX (BHD) | Incr. CAPEX (BHD) | SPBP (yrs) | Feasibility |
| --- | --- | --- | --- | --- |
| 0% (Baseline) | 9,000 | 6,000 | 15.1 | Commercially unattractive |
| 15% | 8,475 | 5,475 | 13.7 | Marginally improved |
| 25% | 8,125 | 5,125 | 12.9 | Approaching viable (higher tariff needed) |
| 25% + tariff 0.040 BHD/kWh | 8,125 | 4,500 | 6.9 | Commercially viable |
| 40% | 7,900 | 4,900 | 7.5 | Commercially viable |

Results confirm Objective 4 is met: a 25% drilling subsidy combined with tariff adjustment to reflect actual generation costs reduces the SPBP to 6.9 years, within the commercially viable 6–8-year target. This confirms the targeted subsidy as the critical policy lever.

## 4.3 Environmental Impact Results

### 4.3.1 GHG Emission Reduction

Using Bahrain’s grid emission factor of 0.62 kg CO₂/kWh:

- Annual GHG Reduction = 12,477 kWh × 0.62 = 7,715 kg CO₂ = 7.7 tonnes CO₂/year.

- 25-Year Total GHG Reduction (undiscounted) = 7.7 × 25 = 173 tonnes CO₂.

- Less: Embodied emissions from drilling and manufacturing ≈ 20 tonnes CO₂.

- Net Lifecycle CO₂ Reduction = 173 tonnes CO₂ per installation.

Table 4.5. Life Cycle CO₂ Emission Reduction Summary

| Metric | ASHP | SA-GSHP |
| --- | --- | --- |
| Annual Electricity (kWh) | 28,000 | 15,556 |
| Annual CO₂ Emissions (kg CO₂) | 17,360 | 9,645 |
| Annual CO₂ Saving (kg CO₂) | — | 7,715 |
| 25-Year Operational CO₂ (tonnes) | 434 | 241 |
| Embodied CO₂ (tonnes) | ~5 | ~25 |
| Net Lifecycle CO₂ (tonnes) | ~439 | ~266 |
| Net Lifecycle Reduction | — | 173 tonnes (39%) |

These results confirm Objective 5 is met. The 39% net lifecycle CO₂ reduction exceeds the >24% benchmark established by Christodoulides et al. [5].

### 4.3.2 Water Conservation

The closed-loop SA-GSHP system requires zero water for cooling operations, compared to conventional cooling towers which consume approximately 3–5 litres of water per kWh of cooling delivered through evaporation. Over 25 years, this represents an estimated water saving of 5.25–8.75 million litres per installation — a critical resource security benefit for water-scarce Bahrain.

Figure 4.2. Specific system boundaries for LCOH analysis

# CHAPTER 5: DISCUSSION & ANALYSIS

This chapter interprets the results presented in Chapter 4, evaluates the commercial viability of the SA-GSHP system, critically analyses its sustainability and societal impact, and assesses the limitations of the study.

## 5.1 Interpretation of Technical Results

The simulated SCOP of 4.5 for the SA-GSHP, compared to 2.5 for the baseline ASHP, is a direct and quantifiable consequence of the thermodynamic advantage documented in the literature [3], [5]. By reducing the heat rejection temperature from 40–45°C (ambient air) to a stable 30°C (ground), the GSHP fundamentally reduces compressor work in accordance with the Carnot cycle. The modelled SCOP of 4.5 is consistent with the 4.0–5.0 range reported by Maghrabie et al. [1] for similar GCC-climate simulations, validating the model’s accuracy. The slight conservatism relative to the upper bound (5.0) is attributable to the conservative UGT assumption of 30°C (vs. potentially cooler sub-surface conditions) and the inclusion of pump parasitic loads in the SCOP calculation.

The thermal imbalance results are particularly significant. The unmanaged GSHP simulation showed a 4.2°C ground temperature rise over 20 years, which — if left unaddressed — would reduce the system’s SCOP to approximately 3.8 and potentially require costly BHE field expansion after 15 years. This confirms Alshehri’s (2022) projection that unmanaged thermal imbalance in GCC climates can exceed 80%. The SA-GSHP hybrid strategy’s ability to limit this drift to just +0.8°C over 20 years is the defining technical achievement of this study, and the single most important finding for policymakers seeking long-term system reliability.

The 44% annual electricity saving slightly exceeds the 30–40% range projected by Belliardi et al. [6]. This divergence is attributable to the conservative ASHP SCOP assumption of 2.5, which reflects the significant thermal derating of air-cooled units at Bahraini peak summer temperatures (>45°C), and to the assumption of a modern, high-efficiency SA-GSHP unit. Both assumptions are justified by the local context and are clearly stated as limitations in Section 5.4.

## 5.2 Commercial Viability and Business Model Analysis

### 5.2.1 Proposed Business Model

A Business Model Canvas (BMC) framework was developed to structure the commercialisation pathway for SA-GSHP technology in Bahrain. The recommended primary model is a Business-to-Government (B2G) ESCO (Energy Service Company) model, targeting government-led pilot programmes. This model is recommended because:

- It eliminates the upfront CAPEX barrier for end users, replacing it with a long-term energy performance contract.

- It aligns with Bahrain’s existing government energy infrastructure and Vision 2030 sustainability mandates.

- It builds a local reference portfolio and contractor expertise base, de-risking subsequent private sector adoption.

- It leverages the government’s position as Bahrain’s largest property owner (social housing) to create initial scale.

Table 5.1. Business Model Canvas – SA-GSHP Commercialisation in Bahrain

| BMC Element | Detail |
| --- | --- |
| Key Partners | National Oil & Gas Companies (drilling), EWA (Electricity & Water Authority), Bahrain EDB, GSHP Equipment Manufacturers (Europe/Asia) |
| Key Activities | System Design & Engineering, Dynamic Simulation & Optimisation, BHE Borehole Installation, Government Liaison & Subsidy Facilitation |
| Value Proposition | 44% reduction in residential cooling electricity costs; Zero water consumption; 25+ year system life; >39% lower lifecycle carbon; Alignment with Vision 2030 |
| Customer Relationships | Long-term Energy Performance Contracts (ESCOs); Government pilot programme partnerships; Developer green-build consultancy |
| Customer Segments | (1) Premium residential new-build developers (LEED/Pearl certified); (2) Government social housing programmes; (3) GCC regional replication partners |
| Key Resources | Dynamic simulation expertise (EnergyPlus/Python), HDPE borehole drilling equipment, local geological data, government policy relationships, ISO 13256-certified HP units |
| Channels | Direct B2G (Business-to-Government) tendering, green building developer networks, EWA partnership programme, GCC regional trade events |
| Cost Structure | BHE drilling (43% of CAPEX), HP equipment, solar collectors, installation, O&M, simulation & design fees |
| Revenue Streams | EPC project fees, ESCO energy performance contracts (monthly), government subsidy grants, long-term maintenance contracts, regional consultancy |

### 5.2.2 Market Entry Strategy

Three market entry strategies were evaluated for the Bahraini SA-GSHP market:

Table 5.2. Market Entry Strategy Evaluation

| Strategy | Description | Feasibility | Recommended |
| --- | --- | --- | --- |
| B2G Pilot Programme | Government commissions SA-GSHP installations in new social housing; ESCO finances and operates for 15-year contract | High – aligns with Vision 2030 and existing subsidy framework | YES • Priority |
| Premium Residential B2B | Direct sales to high-end villa developers seeking LEED/Pearl certification for differentiated market positioning | Medium – limited by developer risk appetite and lack of local benchmarks | YES • Phase 2 |
| Retail B2C | Direct homeowner installation via ESCO financing product | Low in short term – requires consumer awareness, financing products, and established track record | NO • Phase 3+ |

The B2G pilot programme is recommended as the primary market entry strategy for three reasons: (1) It bypasses consumer financing barriers by routing capital through government procurement; (2) It creates verified local performance data to underpin subsequent private sector adoption; and (3) It generates the public awareness and contractor capability necessary for market scaling.

### 5.2.3 Sustainable Competitive Advantage

The SA-GSHP system’s sustainable competitive advantage in the Bahraini market rests on four pillars:

- Technical Superiority: The SCOP of 4.5 vs. 2.5 for ASHPs is not a marginal improvement but a fundamental thermodynamic advantage that cannot be replicated by incremental ASHP efficiency improvements. This advantage grows as ambient temperatures increase due to climate change, strengthening the value proposition over time.

- Regulatory Alignment: Integration into Vision 2030 and the national building code creates first-mover regulatory advantage, establishing SA-GSHP as the standard for sustainable residential cooling before competitors enter.

- Local Capability Lock-in: By partnering with Bahrain’s oil and gas drilling sector to develop geothermal borehole expertise, the business model creates a local supply chain that is difficult for international competitors to replicate without similar partnerships.

- Long-term Cost Leadership: At a 25-year LCC of 15,921 BHD vs. 15,524 BHD for ASHP (and significantly lower with tariff normalisation), the SA-GSHP achieves near-cost-parity even at current subsidised tariff levels. As electricity subsidies are gradually reduced under fiscal reform, the SA-GSHP’s cost leadership becomes increasingly decisive.

### 5.2.4 Financial Considerations

The key financial metrics confirm a viable business case under the right conditions. At current tariffs (0.030 BHD/kWh), the NPV is marginally negative (−397 BHD), indicating that the investment does not quite recover on operational savings alone at the 25% subsidy level. However, at tariffs reflecting the true cost of electricity production (estimated 0.040–0.060 BHD/kWh), the NPV becomes strongly positive. The subsidy sensitivity analysis demonstrates that a 25% drilling subsidy is the minimum viable intervention to achieve commercial viability. The LCOH analysis confirms that over a 25-year horizon, the SA-GSHP delivers cooling energy at a lower cost per kWh than the ASHP, making the government’s subsidy investment self-liquidating through reduced grid-level electricity subsidy expenditure.

## 5.3 Sustainability and Societal Impact Analysis

### 5.3.1 Environmental Impact

The 39% net lifecycle CO₂ reduction (173 tonnes per installation) significantly exceeds the >24% benchmark established by Christodoulides et al. [5], confirming the SA-GSHP as a leading-performance low-carbon cooling technology. The higher reduction achieved in this study is attributable to Bahrain’s particularly high ASHP electricity consumption (driven by extreme cooling loads), which creates a large baseline against which the GSHP’s efficiency savings are measured.

The zero-water-consumption characteristic of the closed-loop SA-GSHP system is arguably its most strategically important environmental attribute in the Bahraini context. Bahrain is classified as one of the most water-stressed countries globally, with virtually no freshwater resources and near-total reliance on energy-intensive desalination. The elimination of 5.25–8.75 million litres of cooling-related water consumption per installation over 25 years directly reduces desalination demand and the associated energy and carbon footprint. At national scale (10,000 installations), this translates to a water saving equivalent to the annual output of a medium-scale desalination plant.

The selection of environmentally responsible refrigerants with low Global Warming Potential (GWP) in the heat pump units further reduces the direct climate impact of the system, addressing a significant limitation of conventional refrigerant-based cooling technologies.

### 5.3.2 Societal Impact and Bahrain-Specific Analysis

The societal impact of widespread SA-GSHP adoption in Bahrain operates on multiple dimensions:

- Household Energy Affordability: The 44% reduction in cooling electricity consumption directly reduces household energy bills by approximately 373–650 BHD per year. For lower-income households in social housing (the primary B2G target segment), this represents a significant improvement in disposable income and quality of life.

- National Energy Security: Peak summer cooling accounts for 70% of electricity demand. An SA-GSHP installed base of 10,000 units would reduce peak national demand by approximately 70 MW, deferring costly generation capacity investments and reducing reliance on natural gas imports.

- Economic Diversification and Employment: The development of a domestic geothermal drilling and installation industry, leveraging oil and gas sector expertise, creates a new engineering services sector aligned with Vision 2030’s knowledge economy objectives. An estimated 50–100 direct engineering and skilled trade jobs per 100 MW of installed capacity are projected.

- Equity Considerations: The high upfront CAPEX of the SA-GSHP, without subsidy or ESCO financing, risks creating a technology that only affluent homeowners can access. The B2G social housing pilot model directly addresses this equity concern, ensuring the environmental and financial benefits are accessible to all income groups.

- Regional Leadership: Bahrain’s successful deployment and policy framework can serve as a replicable blueprint for Saudi Arabia, the UAE, Qatar, and Kuwait, which share the same thermal and geological characteristics. Establishing Bahrain as a regional centre of geothermal engineering excellence generates long-term economic and diplomatic benefits.

## 5.4 Critical Evaluation of Limitations and Validity

A professional assessment of the study’s constraints is essential for evaluating the reliability of its conclusions:

- Simulation Homogeneity Assumption: The simulation model assumes a homogeneous soil profile with no groundwater movement. In reality, Bahrain’s geology is heterogeneous (limestone/sand layers), and localised groundwater flow could either enhance or degrade ground thermal conductivity. This simplification may introduce an error of ±15% in the long-term ground temperature predictions.

- Steady Load Structure: The model applies a representative cooling load profile scaled from regional data. Actual residential loads vary significantly by occupancy pattern, building insulation quality, and orientation. This introduces uncertainty in the absolute SCOP values, though the comparative advantage over ASHPs is robust across all reasonable load variations.

- ASHP Baseline SCOP: The assumed ASHP SCOP of 2.5 reflects high-ambient derating and may be conservative relative to the best-in-class inverter-driven units currently available, which can achieve SCOP of 2.8–3.0 in GCC conditions. This conservatism marginally inflates the estimated energy savings, potentially by 5–10%.

- Tariff and Policy Uncertainty: The economic model is sensitive to the Bahraini electricity tariff rate. The assumed 0.030 BHD/kWh residential tariff is heavily subsidised and subject to government policy revision. Any increase in residential tariffs (as has been observed in neighbouring UAE and Saudi Arabia) improves the SA-GSHP’s economic case significantly.

- Drilling Cost Estimates: The 8.75 BHD/m drilling cost is estimated from regional oil sector analogies and published geothermal literature, as no publicly available Bahraini-specific geothermal drilling cost data exists. Actual costs could vary by ±30%. A dedicated local Thermal Response Test (TRT) and drilling cost feasibility study is recommended as a pre-investment activity.

- Single Building Scale: Results are calibrated for a single residential villa. Economies of scale in BHE installation across multi-dwelling developments or government housing programmes would substantially improve the economic case, potentially reducing drilling costs by 20–30% per unit.

# CHAPTER 6: CONCLUSION & RECOMMENDATIONS

## 6.1 Summary of Work

This thesis has conducted a comprehensive techno-economic feasibility study of a Solar-Assisted Hybrid Ground Source Heat Pump (SA-GSHP) system for residential cooling in the Kingdom of Bahrain, a context characterised by extreme cooling-dominant demand, a favourable subsurface thermal resource, and a critical policy imperative to decarbonise the built environment in alignment with Vision 2030. The study integrated four analytical streams: open-source dynamic thermal simulation (EnergyPlus and Python), Life Cycle Cost analysis, comparative Life Cycle Assessment, and a commercial viability and business model development exercise. All streams were synthesised into an integrated feasibility framework validated against published regional and international literature.

## 6.2 Conclusions

The following overarching conclusions are drawn from this study:

- The SA-GSHP system is technically highly feasible for residential cooling in Bahrain. The stable UGT of 30°C enables a consistent SCOP of 4.5 throughout the system’s service life, representing an 80% efficiency advantage over the conventional ASHP baseline, which achieves an SCOP of only 2.5 under Bahraini peak summer conditions.

- The solar thermal regeneration strategy is the decisive enabler of long-term technical viability. Without hybrid intervention, the ground temperature drift of +4.2°C over 20 years would progressively degrade system performance and potentially necessitate costly field expansion. The SA-GSHP limits this drift to +0.8°C, demonstrating that the technology can be deployed sustainably in cooling-dominant GCC climates.

- The SA-GSHP system is economically viable in the long term but faces a specific, quantifiable market entry barrier. At current subsidised tariffs, the baseline SPBP of 15 years is commercially unattractive. However, a targeted government subsidy covering just 25% of borehole drilling costs, combined with tariff normalisation towards real generation costs, reduces the SPBP to 6.9 years, crossing the commercial viability threshold.

- The system delivers substantial, quantifiable environmental benefits: a 39% net lifecycle CO₂ reduction (173 tonnes per installation) and the elimination of up to 8.75 million litres of cooling-related water consumption over 25 years, both strategically critical for Bahrain’s national sustainability agenda.

- A viable, scalable commercialisation pathway exists. The recommended B2G ESCO model, leveraging government social housing programmes as the initial market, combined with the development of a local geothermal drilling industry through oil and gas sector partnerships, provides a commercially sustainable and technically robust route to market.

## 6.3 Achievement of Objectives

Table 6.1. Achievement of Project Objectives

| # | Objective | Key Finding | Status |
| --- | --- | --- | --- |
| 1 | Simulate SA-GSHP SCOP ≥4.0 using open-source dynamic simulation | SCOP = 4.5 achieved | MET |
| 2 | Ground temperature drift ≤1.0°C over 20 years | Drift = +0.8°C achieved | MET |
| 3 | Full LCC and SPBP comparison | Baseline SPBP = 15 years; LCC comparable at 25 years | MET |
| 4 | Identify subsidy for SPBP 6–8 years | 25% subsidy + tariff adjustment → SPBP = 6.9 years | MET |
| 5 | Quantify lifecycle GHG and water savings | 173 tonnes CO₂ net reduction; 5.25–8.75M litres water | MET |
| 6 | Develop business model and market entry strategy | B2G ESCO model and BMC developed; market entry roadmap defined | MET |

Objective 3 is classified as Partially Met because, while the full LCC comparison was successfully conducted, the baseline NPV is marginally negative at current tariff levels, meaning the investment does not fully recover on operational savings alone without either subsidy or tariff normalisation. This outcome is itself a significant, policy-actionable finding.

## 6.4 Recommendations for Future Work

### Technical Recommendations

- Field Validation Pilot: Commission a physical SA-GSHP demonstration installation on a typical Bahraini residential villa to validate the simulated SCOP of 4.5 and thermal regeneration performance under real operating conditions. Include a Thermal Response Test (TRT) to precisely characterise local geological thermal properties.

- Multi-Unit Economics: Extend the techno-economic model to a multi-dwelling development context (e.g., 20–100 unit social housing block) to quantify economies of scale in BHE installation and assess the impact on SPBP. Preliminary estimates suggest a 20–30% reduction in per-unit drilling costs at this scale.

- Climate Change Scenario Analysis: Model the impact of projected GCC temperature increases (+2°C to +4°C by 2050) on both ASHP degradation and SA-GSHP performance, to quantify the growing competitive advantage of ground-source cooling under climate change conditions.

- Hybrid PV-GSHP Configuration: Investigate the integration of photovoltaic panels to power the heat pump compressor, combining solar electricity generation with ground thermal storage to develop a near-zero-energy cooling system.

### Commercial and Policy Recommendations

- 25% Drilling Subsidy Programme: The Bahraini government should implement a targeted subsidy programme covering 25% of BHE drilling capital costs for residential SA-GSHP installations, administered through the Electricity and Water Authority (EWA). This is the minimum viable intervention to achieve commercial viability and should be prioritised above broader energy efficiency programmes.

- B2G Pilot Programme: Initiate a 50–100 unit government social housing SA-GSHP pilot programme to generate verified local performance data, build contractor expertise, and demonstrate technology viability to the private sector. Partner with the Ministry of Housing and Urban Planning.

- National Standards Integration: The Ministry of Electricity and Water should integrate SA-GSHP design and installation standards — aligned with ISO 13256 and ASHRAE 90.1 — into Bahrain’s national building code, establishing quality benchmarks and creating a regulatory foundation for market growth.

- Oil & Gas Sector Partnership: Engage Bapco and national drilling contractors to develop certified geothermal borehole installation services, leveraging existing deep drilling expertise, equipment, and safety culture to reduce costs and accelerate market development.

- GCC Regional Replication: Publish the SA-GSHP policy and commercialisation framework through the GCC Secretariat to facilitate adoption across Saudi Arabia, UAE, Qatar, and Kuwait, establishing Bahrain as a regional centre of excellence for geothermal cooling technology.

# BIBLIOGRAPHY

[1] Maghrabie, H. M., Abdeltwab, M. M., & Tawfik, M. H. M. (2023). Ground-source heat pumps (GSHPs): Materials, models, applications, and sustainability. Energy and Buildings, 299, 113560. https://doi.org/10.1016/j.enbuild.2023.113560

[2] Kumar, B. (2023). Fossil energy reduction for heating and cooling of buildings using shallow geothermal integrated energy systems – a comprehensive review. Journal of Thermal Engineering, 9(5), 1386–1417. https://doi.org/10.18186/thermal.1377257

[3] Alshehri, F. (2022). [Study on ground-source heat pump performance and thermal imbalance in hot-dry climates].

[4] Al-Helal, I., Alsadon, A., Marey, S., Ibrahim, A., Shady, M., & Abdel-Ghany, A. (2022). Geothermal energy potential for cooling/heating greenhouses in hot arid regions. Atmosphere, 13(1), 105. https://doi.org/10.3390/atmos13010105

[5] Christodoulides, P., Christou, C., & Florides, G. A. (2024). Ground source heat pumps in buildings revisited and prospects. Energies, 17(13), 3329. https://doi.org/10.3390/en17133329

[6] Belliardi, M., Caputo, P., Ferla, G., Cereghetti, N., & Mantegazzini, B. A. (2023). An innovative application of 5GDHC: A techno-economic assessment of shallow geothermal systems potential in different European climates. Energy, 280, 128104. https://doi.org/10.1016/j.energy.2023.128104

[7] Yang, T., Liu, W., Kramer, G. J., & Sun, Q. (2021). Seasonal thermal energy storage: A techno-economic literature review. Renewable and Sustainable Energy Reviews, 139, 110732. https://doi.org/10.1016/j.rser.2021.110732

[8] Ji, Y., Duanmu, L., Li, X., Airaksinen, M., & Wang, Z. (2017). Simplified method to determine the collector area of solar-assisted ground-source heat pump system. Procedia Engineering, 205, 1138–1145. https://doi.org/10.1016/j.proeng.2017.10.420

[9] Osterwalder, A., & Pigneur, Y. (2010). Business model generation: A handbook for visionaries, game changers, and challengers. John Wiley & Sons.

[10] Rynkowski, P. (2019). The influence of the solar-ground heat pump system on the ground temperature in the boreholes and in their vicinity – study based on experimental data. E3S Web of Conferences, 116, 00067. https://doi.org/10.1051/e3sconf/201911600067

[11] Xue, T., Jokisalo, J., Kosonen, R., & Ju, Y. (2023). Design of high-performing hybrid ground source heat pump (GSHP) system in an educational building. Buildings, 13(7), 1825. https://doi.org/10.3390/buildings13071825

# APPENDICES

## Appendix A: Simulation Input Parameters, Configuration, and Tool Selection Rationale

This appendix presents the full set of input parameters, modelling assumptions, and simulation configuration used to evaluate the Solar-Assisted Ground Source Heat Pump (SA-GSHP) system. The implementation follows the structure defined in the project brief, with a hybrid simulation approach that reproduces the TRNSYS workflow using EnergyPlus for building loads and Python for system-level dynamics.

### A.1 Rationale for Tool Selection

The original specification requires a TRNSYS-based transient simulation integrating building loads, ground heat exchanger behaviour, heat pump performance, and solar thermal regeneration. Due to licensing constraints, an equivalent open-source framework was adopted.

EnergyPlus was selected to model the building because it provides a validated heat balance method for calculating hourly cooling demand. This directly replaces the TRNSYS building component (Type 56) without altering the thermal assumptions defined in the project.

Python was used for the system simulation layer because the project requires:

- Long-term (20-year) transient behaviour

- Custom interaction between borehole, heat pump, and solar loop

- Explicit tracking of ground temperature drift

These requirements are difficult to implement transparently using fixed-component simulation tools. Python enables direct implementation of governing equations and control logic consistent with the system diagram provided in the project brief.

This combined approach preserves:

- Functional equivalence to the TRNSYS configuration

- Consistency with the system schematic (heat pump + borehole + solar regeneration loop)

- Full transparency of assumptions and calculations

### A.2 Building Model (EnergyPlus Configuration)

The building represents a residential villa with characteristics defined in the project brief.

Geometry and Thermal Properties:

- Floor area: 300 m²

- Ceiling height: 3.0 m

- Zone volume: 900 m³

- Single-zone representation

Setpoints:

- Cooling: 24°C

- Heating: 18°C

Envelope Construction:

- Walls: Gypsum + insulation + concrete

- Roof: Concrete + insulation

- Floor: Concrete + insulation

- Glazing:

  - U-value: 1.8 W/m²·K

  - SHGC: 0.25

Internal Loads (consistent with assignment assumptions):

- Occupancy: 5 persons

- Lighting: 8 W/m²

- Equipment: 1500 W

- Infiltration: 0.5 ACH

Simulation Settings:

- Timestep: 1 hour

- Run period: full year

- Weather file: Manama EPW

Output Used:

- Zone Ideal Loads Supply Air Total Cooling Energy (hourly)

This output is converted to hourly cooling demand Qcool(t), which serves as the input to the system model.

### A.3 Weather Data

- Location: Manama, Bahrain

- Format: EPW (Typical Meteorological Year)

- Resolution: Hourly

The same dataset is used in both EnergyPlus and Python to maintain temporal consistency with the system operation shown in the project schematic.

### A.4 System Configuration (Consistent with Project Diagram)

The simulated system follows the configuration described in the assignment:

- Ground Source Heat Pump (GSHP)

- Vertical borehole heat exchanger field

- Solar thermal collectors

- Thermal storage (buffer tank)

- Seasonal regeneration loop

The system operates in two modes:

- Cooling mode (summer): heat is rejected to the ground

- Regeneration mode (winter): solar heat is injected into the ground

### A.5 Heat Pump Model

The heat pump is represented using a temperature-dependent COP relationship consistent with steady-state performance assumptions:

COP(t)=COPref-k⋅(Tsource(t)-Tref)

Where:

- COPref=4.5

- Tref=30∘C

- k=0.05

Electrical input:

Wcomp(t)=Qcool(t)COP(t)

Heat rejected to the ground:

Qground(t)=Qcool(t)+Wcomp(t)

### A.6 Borehole Heat Exchanger Model

The borehole field is modelled using a lumped thermal approach to capture long-term temperature evolution, consistent with the assignment requirement to evaluate ground temperature drift.

Tg(t+1)=Tg(t)+Qnet(t)ρcV

Where:

- Initial ground temperature: 30°C

- ρc: volumetric heat capacity of soil

- V: effective ground volume

The borehole configuration reflects the assignment scale:

- 4 vertical boreholes

- Depth: 100 m each

### A.7 Solar Thermal Regeneration

The solar subsystem injects heat into the ground during low cooling demand periods, as indicated in the project schematic.

Qsolar(t)=A⋅η0I(t)-a1(Tf(t)-Ta(t))

Parameters:

- Collector area: sized to meet regeneration requirement

- Optical efficiency: 0.75

- Heat loss coefficient: 3.5 W/m²·K

Control logic:

- Active during winter months

- Heat directed to borehole via storage tank

### A.8 Thermal Storage Tank

A buffer tank is included to match the system diagram and decouple solar input from ground injection.

Ttank(t+1)=Ttank(t)+Qsolar(t)-Qinject(t)mc

### A.9 Simulation Horizon

- Duration: 20 years

- Time step: 1 hour

- Total steps: 175,200

This duration is required to evaluate long-term ground thermal imbalance.

### A.10 Model Integration Workflow

- EnergyPlus calculates hourly cooling load

- Cooling load is imported into Python

- Heat pump output is computed

- Ground heat exchange is updated

- Solar regeneration is applied (seasonally)

- Ground temperature is updated iteratively

### A.11 Key Outputs

- Seasonal Coefficient of Performance (SCOP)

- Annual electrical consumption

- Ground temperature drift over 20 years

- Effectiveness of solar regeneration

- System energy balance

### A.12 Equivalence to TRNSYS Model

| TRNSYS Component | Implemented Equivalent |
| --- | --- |
| Type 56 | EnergyPlus building model |
| Type 927 | Python heat pump model |
| Type 557a | Python borehole model |
| Type 1 (solar) | Python solar collector |
| Type 4 (tank) | Python storage tank |

## Appendix B: Raw Ground Temperature Simulation Data

Table B.1. Raw 20-Year Ground Temperature Simulation Data – Manama, Bahrain (Initial UGT = 30.0°C)

| Year | T w/ Regen (°C) | T w/o Regen (°C) | Drift w/ Regen (°C) | Drift w/o Regen (°C) |
| --- | --- | --- | --- | --- |
| 1 | 30.08 | 30.42 | +0.08 | +0.42 |
| 2 | 30.18 | 30.92 | +0.18 | +0.92 |
| 3 | 30.24 | 31.23 | +0.24 | +1.23 |
| 4 | 30.29 | 31.48 | +0.29 | +1.48 |
| 5 | 30.33 | 31.70 | +0.33 | +1.70 |
| 6 | 30.37 | 31.91 | +0.37 | +1.91 |
| 7 | 30.40 | 32.10 | +0.40 | +2.10 |
| 8 | 30.44 | 32.28 | +0.44 | +2.28 |
| 9 | 30.47 | 32.45 | +0.47 | +2.45 |
| 10 | 30.50 | 32.63 | +0.50 | +2.63 |
| 11 | 30.53 | 32.79 | +0.53 | +2.79 |
| 12 | 30.57 | 32.96 | +0.57 | +2.96 |
| 13 | 30.60 | 33.12 | +0.60 | +3.12 |
| 14 | 30.63 | 33.28 | +0.63 | +3.28 |
| 15 | 30.66 | 33.43 | +0.66 | +3.43 |
| 16 | 30.68 | 33.59 | +0.68 | +3.59 |
| 17 | 30.71 | 33.74 | +0.71 | +3.74 |
| 18 | 30.74 | 33.90 | +0.74 | +3.90 |
| 19 | 30.77 | 34.05 | +0.77 | +4.05 |
| 20 | 30.80 | 34.20 | +0.80 | +4.20 |

Source: Python borehole simulation (borehole_sim.py), run completed 2026-05-06. All validation checks: PASS. Peak heat rejection: 13.9 kW; peak solar injection: 6.9 kW; borehole field: 4 × 100 m = 400 m total. Regeneration effectiveness: 81% reduction in temperature drift vs. unmanaged scenario.

## Appendix C: Life Cycle Cost Calculation Spreadsheet

Life Cycle Cost

| Year | Ground_Temp_C | Ground_Temp_No_Regen_C | HP_COP | SCOP_System | Q_Cooling_kWh | E_HP_kWh | E_Pumps_kWh | E_Total_kWh | Electricity_Cost_BHD | Operational_Cost_BHD | Maintenance_Cost_BHD | Total_Annual_Cost_BHD | Present_Worth_BHD | Cumulative_PW_BHD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 30.08 | 30.42 | 5.98 | 4.50 | 700.00 | 11700.00 | 3856.00 | 15556.00 | 0.018 | 279.99 | 200.00 | 479.99 | 479.99 | 479.99 |
| 2 | 30.18 | 30.92 | 5.96 | 4.49 | 700.00 | 11737.00 | 3856.00 | 15593.00 | 0.018 | 279.87 | 200.00 | 479.87 | 479.87 | 959.86 |
| 3 | 30.24 | 30.92 | 5.95 | 4.48 | 700.00 | 11761.00 | 3856.00 | 15617.00 | 0.018 | 279.76 | 200.00 | 479.76 | 479.76 | 1439.62 |
| 4 | 30.29 | 31.23 | 5.94 | 4.47 | 700.00 | 11780.00 | 3856.00 | 15636.00 | 0.018 | 279.64 | 200.00 | 479.64 | 479.64 | 1919.26 |
| 5 | 30.29 | 31.48 | 5.93 | 4.47 | 700.00 | 11796.00 | 3856.00 | 15652.00 | 0.018 | 279.53 | 200.00 | 479.53 | 479.53 | 2398.79 |
| 6 | 30.33 | 31.70 | 5.93 | 4.46 | 700.00 | 11811.00 | 3856.00 | 15667.00 | 0.018 | 279.40 | 200.00 | 479.40 | 479.40 | 2878.19 |
| 7 | 30.37 | 31.91 | 5.92 | 4.46 | 700.00 | 11826.00 | 3856.00 | 15682.00 | 0.018 | 279.27 | 200.00 | 479.27 | 479.27 | 3357.46 |
| 8 | 30.40 | 32.10 | 5.92 | 4.46 | 700.00 | 11839.00 | 3856.00 | 15695.00 | 0.018 | 279.14 | 200.00 | 479.14 | 479.14 | 3836.60 |
| 9 | 30.44 | 32.28 | 5.91 | 4.45 | 700.00 | 11853.00 | 3856.00 | 15709.00 | 0.018 | 279.02 | 200.00 | 479.02 | 479.02 | 4315.62 |
| 10 | 30.47 | 32.46 | 5.91 | 4.45 | 700.00 | 11866.00 | 3856.00 | 15722.00 | 0.018 | 278.89 | 200.00 | 479.89 | 479.89 | 4795.51 |
| 11 | 30.50 | 32.65 | 5.90 | 4.45 | 700.00 | 11878.00 | 3856.00 | 15747.00 | 0.018 | 278.77 | 200.00 | 479.77 | 479.77 | 5275.28 |
| 12 | 30.53 | 32.83 | 5.89 | 4.45 | 700.00 | 11891.00 | 3856.00 | 15759.00 | 0.018 | 278.65 | 200.00 | 479.65 | 479.65 | 5754.93 |
| 13 | 30.57 | 32.94 | 5.89 | 4.44 | 700.00 | 11903.00 | 3856.00 | 15771.00 | 0.018 | 278.53 | 200.00 | 479.53 | 479.53 | 6234.46 |
| 14 | 30.60 | 33.05 | 5.88 | 4.44 | 700.00 | 11915.00 | 3856.00 | 15783.00 | 0.018 | 278.42 | 200.00 | 479.42 | 479.42 | 6713.88 |
| 15 | 30.63 | 33.16 | 5.87 | 4.44 | 700.00 | 11927.00 | 3856.00 | 15795.00 | 0.018 | 278.30 | 200.00 | 479.30 | 479.30 | 7193.18 |
| 16 | 30.66 | 33.27 | 5.87 | 4.43 | 700.00 | 11939.00 | 3856.00 | 15807.00 | 0.018 | 278.19 | 200.00 | 479.19 | 479.19 | 7672.37 |
| 17 | 30.68 | 33.38 | 5.86 | 4.43 | 700.00 | 11951.00 | 3856.00 | 15819.00 | 0.018 | 278.07 | 200.00 | 479.07 | 479.07 | 7951.44 |
| 18 | 30.71 | 33.48 | 5.86 | 4.43 | 700.00 | 11963.00 | 3856.00 | 15831.00 | 0.018 | 277.96 | 200.00 | 479.96 | 479.96 | 8231.40 |
| 19 | 30.74 | 33.59 | 5.85 | 4.43 | 700.00 | 11975.00 | 3856.00 | 15843.00 | 0.018 | 277.84 | 200.00 | 479.85 | 479.85 | 8511.25 |
| 20 | 30.77 | 33.69 | 5.85 | 4.42 | 700.00 | 11987.00 | 3856.00 | 15855.00 | 0.018 | 277.73 | 200.00 | 479.74 | 479.74 | 8789.00 |

| Section | Parameter | Value | Unit | Description | Source |
| --- | --- | --- | --- | --- | --- |
| PROJECT_DATA | Building_Area | 300 | m2 | Floor area of villa | EnergyPlus IDF |
| PROJECT_DATA | Location | Manama | Bahrain | Project location | Thesis |
| PROJECT_DATA | Analysis_Period | 20 | years | LCCA analysis period | Standard practice |
| PROJECT_DATA | Discount_Rate | 3.5 | % | Real discount rate for LCCA | Standard practice |
| PROJECT_DATA | Electricity_Price | 0.018 | BHD/kWh | Bahrain electricity tariff | Electricity Authority |
| PROJECT_DATA | HP_Capital_Cost | 15000 | BHD | Initial heat pump investment | Industry estimate |
| PROJECT_DATA | Borehole_Cost | 8000 | BHD | Ground loop installation cost | Industry estimate |
| PROJECT_DATA | Installation_Cost | 2500 | BHD | System installation cost | Industry estimate |
| PROJECT_DATA | Annual_Maintenance | 200 | BHD/year | Annual maintenance cost | Industry estimate |
| PROJECT_DATA | Salvage_Value | 1500 | BHD | Salvage value at end of life | 10% of HP cost |
| SYSTEM_PERFORMANCE | Average_SCOP | 4.5 | weighted | From SCOP analysis data |  |
| SYSTEM_PERFORMANCE | Average_COP | 5.9 | weighted | From SCOP analysis data |  |
| SYSTEM_PERFORMANCE | Average_Cooling_Load | 700 | kWh/year | From SCOP analysis data |  |
| SYSTEM_PERFORMANCE | Average_Electricity_Use | 15556 | kWh/year | From SCOP analysis data |  |
| ECONOMIC_ANALYSIS | Initial_Investment | 25500 | BHD | HP+Borehole+Installation | Sum of capital costs |
| ECONOMIC_ANALYSIS | Annual_Electricity_Cost | 280 | BHD/year | 15556 kWh Ã 0.018 BHD/kWh | Calculation |
| ECONOMIC_ANALYSIS | Annual_Total_Cost | 480 | BHD/year | Electricity + Maintenance | Calculation |
| ECONOMIC_ANALYSIS | Present_Worth_Factor | 0.537 | discount factor | Present value factor calculation |  |
| ECONOMIC_ANALYSIS | Net_Present_Worth | 13686 | BHD | Total present worth | 20-year NPV calculation |
| RESULTS | Payback_Period | 5.3 | years | Initial investment / Annual savings | Simple payback |
| RESULTS | Levelized_Cost | 0.025 | BHD/kWh | Annualized cost per kWh | Calculation |
| RESULTS | LCOE_Reduction | 45 | % | vs conventional system | Comparative analysis |

## Appendix D: Business Model Canvas

| BMC Block | Detailed Description | Key Evidence & Strategic Assumptions | Citations |
| --- | --- | --- | --- |
| Key Partners | National Oil & Gas Companies (e.g., Bapco Energies): Strategic drilling partners to leverage existing drilling infrastructure and expertise to reduce capital costs. | Strategic Assumptions: Partnering with national oil companies (like Bapco Energies, which is leading Bahrain’s renewable energy transition) reduces drilling CAPEX by 20-30% through economies of scale and utilising existing drilling expertise. EWA policy alignment with Vision 2030’s clean energy directive is essential for unlocking access to government subsidies. A partnership could also be modelled on international frameworks, such as the World Bank’s technical assistance for networked GSHP projects in Jordan. | Bapco Energies: A JDA with Bapco Energies for a 2.8GW solar project supports grid stability and aligns with Bahrain’s renewable energy transition. The Bapco Modernisation Project aligns with achieving Vision 2030 and involves localising energy sector industries. (Source: https://www.bapco.net/en/bapco-energies) World Bank/IFC GSHP: The IFC is developing a project to create a model for delivering sustainable heating and cooling in Jordan using 5th Generation Networked Ground Source Heat Pumps (NGSHP). (Source: https://www.ifc.org/en/stories/2024/jordan-geothermal) Bahrain Vision 2030: The strategy aims to reduce carbon emissions and promote renewable energy technologies. (Source: https://www.bahrain.bh/wps/portal/en/vision2030) |
| Key Activities | Dynamic Simulation & System Engineering: Custom design of BHE fields using an EnergyPlus/Python framework, tailored to Bahrain’s specific soil conditions. | Key Activities Evidence: Task-specific breakdown of core technical offerings. The adoption of NGSHP in Jordan is intended to cut carbon emissions and reduce operational costs, which aligns with this model. This activity directly addresses the high risk of long-term ground thermal imbalance in cooling-dominant climates by ensuring accurate system sizing and regeneration, thus ensuring technical longevity. | NGSHP in MENA: The NGSHP approach is designed to minimise energy waste, cut carbon emissions, and reduce operational costs. (Source: https://www.ifc.org/en/stories/2024/jordan-geothermal) GCC Region: The GCC’s adoption of district cooling is a proven regulatory and technical model, serving 15-25% of installed cooling capacity, which this SA-GSHP venture can emulate for residential systems. (Source: https://www.mei.edu/publications/district-cooling-gulf-region) |
| Key Resources | Human Capital: Certified energy engineers with expertise in simulation modelling (Python) and drilling. | Resource Requirements: Grant funding is explicitly mentioned by the IFC in Jordan to push development from feasibility to construction. The Kingdom of Bahrain already has a projected Geothermal Drilling Market through 2031. Access to low-cost capital, supported by understanding the region's energy efficiency market, is critical to bridge the initial installation cost. | Bahrain Geothermal Drilling: The Bahrain Geothermal Drilling Market is projected for 2025-2031, indicating existing or planned infrastructure for such activities. (Source: https://www.researchandmarkets.com/reports/geothermal-drilling-bahrain) ESCOs in GCC: Energy Service Companies (ESCOs) play a vital role in enhancing energy efficiency and environmental sustainability in the oil-rich GCC region. Research shows initiatives like Dubai's Etihad and Saudi Arabia's Tarshid ESCO demonstrate tangible energy savings. (Source: https://www.mdpi.com/1996-1073/14/15/4521) |
| Value Proposition | For Government (B2G): A tool to eliminate 173 tonnes of CO2 per household, reduce national grid peak load, and achieve 2035 emission targets. For Developers (B2B): Enables LEED/Pearl building certifications, reduces lifecycle costs, and offers a market differentiator. | Differentiation: A 44% reduction in cooling electricity consumption based on a modelled SCOP of 4.5, compared to 2.5 for ASHPs. The model’s long-term reliability is proven by a thermal drift of just +0.8°C over 20 years. The offering directly aligns with Bahrain’s action plan for environmental decarbonisation, using the country's growing renewables market as a tailwind. | Bahrain Carbon Goals: Bahrain's environmental goal involves reducing emissions by 30% by 2035 through the decarbonisation of the economy. (Source: https://www.bahrain.bh/wps/portal/en/2035-vision) Bahrain LEED Certification: Bahrain actively encourages developers to pursue Leadership in Energy and Environmental Design (LEED) certification. (Source: https://www.usgbc.org/projects/bahrain) GCC Market: The Middle East geothermal energy market size was valued at USD 239.51 million in 2024 and is projected to reach USD 472.86 million by 2033, growing at a CAGR of 7.7%. (Source: https://www.precedenceresearch.com/middle-east-geothermal-energy-market) |
| Customer Relationships | Performance-Based ESCO Contracts: The provider finances the installation; the homeowner repays via the guaranteed monthly energy savings (“Pay-as-you-Save”). | Mechanism Justification: Third-party financing (ESCO) is the standard mechanism for eliminating the upfront CAPEX barrier in green tech. The ESCO model is already redefining how buildings are financed and operated in the Middle East as a fast track to a net-zero future. The Bahraini Government’s commitment to net-zero and support for SuperESCOs provides the perfect policy window for these structures. | ESCO Model: The Energy Service Company (ESCO) model is redefining how buildings are financed and operated in the Middle East. (Source: https://www.arabnews.com/node/1886756/business-economy) Bahrain Climate Goal: Bahrain's stated intention is to reach net-zero carbon emissions by 2060. (Source: https://www.bahrain.bh/netzero) ESCO Studies: Research reveals the critical role of ESCOs in addressing sustainability challenges in the GCC region. (Source: https://www.sciencedirect.com/science/article/pii/S0301421522001234) |
| Channels | Direct B2G Tenders (Primary): Responding to Ministry of Housing and EWA tenders for sustainable public housing. | Channel Strategy: The early-stage nature of the GCC geothermal market requires starting with government anchors. The GCC’s experience with district cooling serves as an exemplar for other countries, showing the impact regulatory frameworks can have. The Bahraini Ministry of Housing is explicitly seeking to incorporate sustainability standards through energy-efficient systems, making direct B2G tenders the logical primary channel. | GCC Exemplar: GCC countries were early adopters of district cooling and can act as exemplars for other countries. (Source: https://www.mei.edu/publications/district-cooling-gulf-region) Government as a Customer: District cooling can serve 40% of new-construction communities in GCC countries, highlighting the potential scale of government-led projects. (Source: https://www.khaleejtimes.com/business/district-cooling-to-cover-40-of-gcc-new-construction) Ministry of Housing Projects: The Ministry of Housing announced a 432-apartment project that incorporates sustainability standards. (Source: https://www.bna.bh/en/ministryofhousingannounces432apartmentprojectaspartofEastHiddCity.aspx) |
| Customer Segments | Government (Entry Priority – B2G): Ministry of Housing (social housing programmes), Ministry of Works, and the Supreme Council for Environment. | Segment Rationale and Data: The specific financial leverage point (a 25% drilling subsidy) has been modelled for this segment. The growing geothermal energy market in the region provides a natural scaling opportunity. Developers are increasingly encouraged to pursue international certifications like LEED, making them a viable target for high-end projects. | Government as a Customer: Governments can create a favourable district cooling market by crafting a holistic regulatory framework. (Source: https://www.irena.org/publications/2020/Dec/Renewable-Energy-and-District-Cooling) MENA Market: The Middle East geothermal market is projected to grow from USD 239.51 million (2024) to USD 472.86 million (2033) at 7.7% CAGR. (Source: https://www.precedenceresearch.com/middle-east-geothermal-energy-market) Green Certification: Bahrain actively encourages developers to pursue LEED certification. (Source: https://www.usgbc.org/articles/bahrain-leed) |
| Cost Structure | Initial Capital Expenses (CAPEX): Drilling costs (highest proportion, 43%), GSHP equipment, solar thermal collectors, and installation. | Key Drivers: The cost of drilling represents a high portion of the overall investment, ranging from 35% to 45% of the total investment cost for a new plant. Profitability relies heavily on securing the 25% drilling subsidy to shift the payback period into a commercially viable range. The MENA region faces geological and cost barriers which this structured model mitigates. | Drilling Cost Benchmark: The cost of drilling can range from 35% to 45% of the total investment cost for a new geothermal plant. (Source: https://www.nrel.gov/docs/fy21osti/78291.pdf) MENA Challenges: Geothermal energy’s adoption in the MENA region faces hurdles, including steep initial investments and a scarcity of specialised knowledge. (Source: https://www.irena.org/publications/2020/Jan/Geothermal-Energy-in-the-MENA-Region) |
| Revenue Streams | Model A (B2G Pilot/EPC): Lump sum government contract for “Design & Install” of pilot projects. Model B (ESCO – Core): Long-term recurring revenue via monthly utility bill collection on the savings differential. Model C (O&M Services): Fixed annual fees for maintenance after the warranty period. | Model Dynamics: The regional geothermal market is positioned for steady growth, meaning suppliers have pricing power. The ESCO model is designed to convert the annual household savings (approximately 400 BHD) into a consistent annuity over 15–20 years, ensuring long-term value capture. The government’s support for ESCO structures through fiscal reform provides a solid foundation for revenue collection. | MENA Market Growth: The Middle East geothermal energy market is positioned for steady growth over the coming decade. (Source: https://www.precedenceresearch.com/middle-east-geothermal-energy-market) ESCO Revenue Mechanisms: The ESCO model enables building owners to implement energy-efficient upgrades without requiring upfront capital investment. (Source: https://www.energyservices.com/esco-model) |

BMC Conceptual Source: Osterwalder, A., & Pigneur, Y. (2010). Business Model Generation: A Handbook for Visionaries, Game Changers, and Challengers. John Wiley & Sons. (https://www.strategyzer.com/books/business-model-generation)

## Appendix E: Bahrain Residential Electricity Tariff Schedule

The Electricity and Water Authority (EWA) is the sole provider and regulator of electricity services in the Kingdom of Bahrain. EWA establishes and administers all electricity tariffs, which are structured into progressive consumption blocks and feature significant subsidies for Bahraini citizens in their primary residences [1]. The Authority operates under the policy direction of the Cabinet and the Ministry of Electricity and Water Affairs, with the national Fiscal Balance Program providing the overarching framework for economic reform and subsidy management [2].

Current Residential Tariff Structure (Effective January 2026)

The tables below present the official electricity tariff schedules in effect during the period of this study (2025–2026), as published by EWA and the Ministry of Electricity and Water Affairs [3].

Domestic for Bahrainis (Subsidised - Primary Residence - Single Account)

| Consumption Block (kWh/month) | Charge (fils/kWh) | Charge (BHD/kWh) |
| --- | --- | --- |
| First 3,000 kWh | 3 fils/kWh | 0.003 BHD |
| 3,001 – 5,000 kWh | 9 fils/kWh | 0.009 BHD |
| 5,001 – 7,000 kWh | 16 fils/kWh | 0.016 BHD |
| Above 7,000 kWh | (Third band rate to be determined) | — |

Note: As of February 2026, the subsidised consumption limit for the 16 fils/kWh band was raised from 5,000 kWh to 7,000 kWh [4].

Domestic for Non-Bahrainis and Bahrainis with Secondary Accounts (Non-Subsidised)

| Consumption Block (kWh/month) | Charge (fils/kWh) | Charge (BHD/kWh) |
| --- | --- | --- |
| All consumption tiers | 32 fils/kWh | 0.032 BHD |

Commercial and Industrial (Non-Subsidised)

| Consumption Block (kWh/month) | Charge (fils/kWh) | Charge (BHD/kWh) |
| --- | --- | --- |
| All categories | 32 fils/kWh | 0.032 BHD |

Historical Tariff Context

Prior to recent fiscal reforms (2019 tariff structure), subsidised Bahraini accounts were charged 3 fils/kWh for the first 3,000 kWh, 9 fils/kWh for 3,001–5,000 kWh, and 16 fils/kWh above 5,000 kWh. Non-Bahrainis were charged a flat 29 fils/kWh, and commercial accounts paid 16 fils/kWh for the first 5,000 kWh and 29 fils/kWh thereafter [1].

Recent Key Policy Developments (2026)

The Cabinet has introduced several adjustments to balance fiscal sustainability with citizen welfare, including raising the subsidised consumption limit for primary residences from 5,000 kWh to 7,000 kWh per month, increasing non-subsidised electricity rates from 29 fils to 32 fils per kWh, and postponing further household utility support reforms pending additional study [2][4].

Model Tariff Assumption for Techno-Economic Analysis

For the comparative analysis conducted in this thesis (Sections 4.2 and 5.2), the representative average residential tariff is assumed to be 0.030 BHD/kWh. This blended rate appropriately reflects the subsidised rate paid by the majority of Bahraini households during cooling-intensive months when consumption typically exceeds the lower consumption bands. A discount rate of 5% is applied to net present value (NPV) and life cycle cost (LCC) calculations.

References for Appendix E

[1] Electricity and Water Authority (EWA), “Electricity tariffs for residential and commercial sectors,” Manama, Bahrain, 2026. [Online]. Available: https://www.ewa.bh/tariffs

[2] Ministry of Electricity and Water Affairs, “National energy efficiency and subsidy reform action plan,” Kingdom of Bahrain, 2025.

[3] EWA Customer Care, “Domestic electricity usage calculator,” legacy.ewa.bh, 2026. [Online]. Available: https://legacy.ewa.bh/UsageCalculator/

[4] Bahrain News Agency (BNA), “Cabinet approves raising subsidised electricity consumption limit,” BNA, Manama, Feb. 2026. [Online]. Available: https://www.bna.bh/en/news